Would it be possible to get some assistance in understanding the calculation method for Equation IW.5.5.3.2 in STD-SPE-G-011

I believe to calculate Sss it is required to utilise simultaneous equations with Manning’s equation and Equation IW.5.5.3.2, to determine the min Slope (Sss) and resolve the other unknown variable ‘y’ (y is depth of flow, which is found when expanding Rp hydraulic radius and ‘A’ cross-sectional area of flow in pipe)

To provide context:

Circular pipe, radius: r, (m) = given

PDWF: Q, (L/s) = given

TPF (total pumped flows) = 0

Mannings equation

Q = A*v = A * (kn / n ) * ( Rp )2/3 * S1/2

Where,

Q = flow, (L/s)

A = cross sectional area of flow, (m2)

kn = 1

n = 0.012 , mannings roughness coefficient (Taken from STD-SPE-G-011 Table IW.3 as either 0.012 or 0.011.  Chose 0.012 as that seems to be the more conservative of the two)

Rp = Hydraulic radius, (m)

S = Slope, (m/m)

Equation IW.5.5.3.2  from STD-SPE-G-011

Sss = 0.0338 / Rp

Where, 
Sss = minimum grade for sulphide slime control, (%)

Rp = Hydraulic radius, (m) (Noting in use of this equation, it is to be the hydraulic radius at 75% of PDWF)

----------------------------------------

Noting Rp = A/P

Where,

A = cross sectional area of flow, (m2)

P = Wetted Perimeter, (m)

Noting Rp for pipes full or half full simplifies to Rp = r / 2

And for circular pipes under 50% full,

Rp = A/P

Where,

A = r2 * ( θ – sin (θ) ) / 2

P = r * θ

Where, 
θ = 2 * arccos ( (r – y) / r )

Where, 
y = depth of flow, (m)

And for circular pipes over 50% full,

Rp = A/P

Where,

A = π * r2 – (r2 * ( θ – sin (θ) ) / 2 )

P = (2 * π * r ) – ( r * θ)

Where, 
θ = 2 * arccos ( (y + r) / r )

Where,

y = depth of flow, (m)

--------------------------------------------------

Therefore, simultaneous equations of mannings equation and Equation IW.5.5.3.2, should be the solution to resolve the two unknown variables ‘S’ and ‘y’ (y is from fully expanded Rp and A), which would provide the minimum grade for sulphide slime control of a given flow within a chosen pipe size.

But when undertaking the simultaneous equations, the result I am obtaining is unrealistic and the math involved is tedious.

General methodology:

In the context of relating Equation IW.5.5.3.2 and Mannings equation:

Q is to be 0.75 * PDWF , as explained in Equation IW.5.5.3.3 from STD-SPE-G-011

And thus Rp in both equations will be equivalent as describing the same situation.

And additionally, Sss/100 is to be equal to S. (IE (0.0338 / Rp)/100 = m/m units.  With the /100 being to return Sss to SI units, as it is expressed as a %).

- Substitute Equation IW.5.5.3.2 into Mannings equation as ‘S’ to eliminate ‘S’, so that the only unknown variable is ‘y’.

- Solve for ‘y’

- Substitute this ‘y’ value back into Equation IW.5.5.3.2 OR Mannings equation to obtain ‘S’ (minimum slope).

--------------------------

Noting, have only been concerned with minimum slope calculated from Sss, as opposed to Ssc or Smin which are also referenced in STD-SPE-G-011, because Sss appears to be the most conservative (IE giving the steepest minimum grade)

---------------------

References:

Microsoft Word - STD-SPE-G-011 WSA 02 Gravity Sewerage Code Of Australia supplement (iconwater.com.au)

Manning's Formula and Gravity Flow (engineeringtoolbox.com)

https://www.bing.com/ck/a?!&&p=712261ea28e0eff8JmltdHM9MTY4MzA3MjAwMCZpZ3VpZD0wODY5NGUxYy05M2Y4LTY2MDMtM2UxMC01YzY0OTdmODYwMTEmaW5zaWQ9NTE4MA&ptn=3&hsh=3&fclid=08694e1c-93f8-6603-3e10-5c6497f86011&psq=Partially+Full+Pipe+Calculations+Spreadsheet_S.I.+Units&u=a1aHR0cHM6Ly9wZGhsaWJyYXJ5LmNvbS9zaXRlcy9kZWZhdWx0L2ZpbGVzLzIwMTgwMjEtUGFydGlhbGx5JTIwRnVsbCUyMFBpcGUlMjBGbG93JTIwQ2FsY3VsYXRpb25zLnBkZg&ntb=1

WSAA Gravity Sewerage Code of Australia

AS3500.2