## README
Sewer minimum / maximum grade calculator - Icon Water (ACT) STD-SPE-G-011
Replaces '230508 - Sewer Calcs - Peak Flows, Max Grade, Min Grade - DC.xlsx' (left untouched).
WHAT IT DOES
ACT only. Given a design PDWF (from EP, or typed in) it returns, for each pipe size DN150-DN900, Icon Water's slime-control grade Sss, self-cleansing grade Ssc, the governing minimum (with the absolute minimum), the maximum grade (V_max at PDWF) and a capacity check at PWWF.
HOW TO USE
1. 'Peak Flows': enter precincts (dwellings, area). PDWF / GWI / IIF / PWWF follow the WSA 02 Appendix B model; every coefficient is on 'Parameters'.
2. 'Grade Calculator': pick the precinct (or type an EP, or PDWF and PWWF directly). Read Smin / Smax per DN. Yellow = input, green = result.
3. 'Design Table': the reverse direction - pick DN and depth ratio y/D and read the PDWF that corresponds to it and the grade. No iteration; good for charts and cross-checking.
4. 'Parameters': n, K_sss, K_sc, f_sss, f_sc, V_max and the flow coefficients.
5. 'Validation': reproduces the three cases the original sheet solved in Wolfram Alpha.
METHOD (why no Wolfram Alpha is needed)
Icon Water Eq IW.5.5.3.2 is a tractive-force criterion: Sss (%) = 0.0338 / Rp <=> S = K / Rp with K = 0.000338 m, i.e. boundary shear stress tau = rho g Rp S = 3.32 Pa.
Substituting S = K/Rp into Manning V = (1/n) Rp^(2/3) S^(1/2) removes S entirely: V = (1/n) sqrt(K) Rp^(1/6) and Q = (1/n) sqrt(K) A Rp^(1/6).
Writing the part-full circle with the central angle theta (A = D^2 (theta - sin theta)/8, P = D theta/2, Rp = (D/4)(1 - sin theta/theta)) makes every quantity explicit and valid for ANY depth (the original was limited to y < r). Only theta must be found from Q. Because f(theta) = A Rp^(1/6) is very nearly a power law in theta, a Newton step in log-space (theta <- theta (T/f)^(1/p), p = d ln f / d ln theta) converges quadratically from an asymptotic starting value; 14 steps give better than 1e-6 up to y/D = 0.97. Sheet 'Calc' does exactly this - no Goal Seek, macros or circular references.
Dimensionless form: q* = Q n / (sqrt(K) D^(13/6)) = a(theta) r(theta)^(1/6), a = (theta - sin theta)/8, r = (1 - sin theta/theta)/4. One curve serves all diameters; Sss = K / (D r(theta)). At small depths Sss ~ D^0.3 Q^-0.6 (compare Mara & Broome 2008 / NBR 9649: i_min = 0.0055 Q^-0.47 at fixed y/D).
Maximum grade: A = PDWF / V_max -> theta from A -> Rp -> Smax = (V_max n / Rp^(2/3))^2.
Capacity: Manning normal depth at PWWF for the governing grade (same Newton scheme with m = 2/3); Qfull = (1/n)(pi D^2/4)(D/4)^(2/3) S^(1/2).
CHANGES FROM THE ORIGINAL SHEET
- y is no longer typed in from Wolfram Alpha; solved in-sheet for all sizes (original had values for DN150/DN300 only, the rest #DIV/0!).
- Max grade uses V_max = 3.0 m/s at PDWF as the original's own note requested (was 2.9 m/s with PWWF).
- Added Ssc and the absolute minimum so the governing grade is reported (original only did Sss).
- Added capacity check at PWWF, 1-in-X grades, status flags (surcharge, Smax < Smin, pipe too small).
- Peak flows: EP/dwelling looked up from density; #DIV/0! for zero-dwelling precincts removed; IIF density factor now uses EP/ha and a cap at 1.0 as WSA 02 App B specifies (original used dwellings/ha and dropped the factor only for > 150 dw/ha); GWI PortionWet applied once (original 0.01875 x 0.75 = 0.025 x 0.75 x 0.75); added WSA 02 App B d(area) peaking-factor option and a 'combined system' row.
- Sizes extended to DN900; all coefficients moved to named parameters.
CHECKED AGAINST STD-SPE-G-011 VERSION 5 (8 OCTOBER 2025)
Grades: Ssc = 0.0135/Rp, Sss = 0.0338/Rp, both at Qdmp = 0.75 x (PDWF + 2/3 TPF). Absolute minimum above DN150 is 80/ID (mm). DN150 is Table IW.4 by number of houses. Maximum grade is 3.0 m/s at PDWF. Roughness is Table IW.3.
Flows: EP/dwelling is Table IW.1 (3.5 / 2.5 / 2.0). PDWF = 5.83 x ADWF / TEP^0.1. GWI = 0.01875 x area x 0.75. RDI = 0.028 x AEff x 1.2 x I, with I = BOM 1-hour 39.35% AEP intensity x (40/area)^0.12 x 1.5.
Still site-specific: replace 21.4 mm/h with the Bureau of Meteorology 1-hour 39.35% AEP intensity for the catchment. The supplement illustrates the lookup for central Canberra; it does not print 21.4 as the design value.

## Parameters
Parameters (yellow = editable input)
All calculation sheets reference these cells by defined name (Formulas > Name Manager).
Parameter | Symbol / name | Value | Units | Source / note
Hydraulics - Icon Water STD-SPE-G-011 (supplement to WSA 02-2014)
Manning roughness coefficient (Icon) | n | 0.012 | - | STD-SPE-G-011 Table IW.3 gives 0.011 / 0.012 by material; 0.012 is the conservative value used in the original sheet.
Sulphide slime control coefficient | K_sss | 0.0338 | % x m | Eq IW.5.5.3.2: Sss (%) = 0.0338 / Rp, Rp = hydraulic radius at f_sss x PDWF. Equivalent boundary shear stress tau = K/100 x rho x g = 3.32 Pa.
Flow fraction for slime control | f_sss | 0.75 | - | Eq IW.5.5.3.3: Rp evaluated at 0.75 x PDWF (TPF = 0).
Self-cleansing coefficient | K_sc | 0.0135 | % x m | Eq IW.5.5.3.1: Ssc (%) = 0.0135 / Rp. Same Rp as slime control (Eq IW.5.5.3.3).
Flow fraction in Qdmp | f_sc | 0.75 | - | Eq IW.5.5.3.3: Qdmp = 0.75 x (PDWF + 2/3 TPF). Both Ssc and Sss use Rp at this flow. f_sss is the same factor.
Maximum velocity | V_max | 3 | m/s | IW.5.5.4: maximum grade is the grade at which velocity at PDWF reaches 3.0 m/s. The original sheet used 2.9 m/s with PWWF and carried a note to change to 3.0 m/s and PDWF.
Water density | rho | 1000 | kg/m3 | Shear-stress equivalents only.
Gravity | g | 9.81 | m/s2 | Shear-stress equivalents only.
Shear stress equivalent of K_sss | tau_sss |  | Pa | Derived - information only.
Shear stress equivalent of K_sc | tau_sc |  | Pa | Derived - information only.
Flow estimation - STD-SPE-G-011 Version 5 (8 Oct 2025), Section IW.3
ADWF loading | PCC | 180 | L/EP/day | WSA 02 App B2: ADWF = 0.0021 L/s/EP = 180 L/d/EP.
Peaking factor method (1 = a x EP^-b as original; 2 = WSA 02 App B d(area) polynomial) | PF_method | 1 | - | Icon requires method 1: Eqn 3.4.2.3, PDWF = 5.83 x ADWF / TEP^0.1. Method 2 is the old WSA area polynomial and is not used by Icon.
Peaking factor coefficient (method 1) | PF_a | 5.83 | -
Peaking factor exponent (method 1) | PF_b | 0.1 | -
Groundwater infiltration rate | GWI_rate | 0.01875 | L/s/ha | Eqn 3.4.3.1: GWI = 0.01875 x NSA x Portionwet.
Portion of network below groundwater | PortionWet | 0.75 | - | Icon default Portionwet = 0.75, applied once on top of the 0.01875 coefficient.
IIF (RDI) coefficient | IIF_coef | 0.028 | - | WSA 02 App B4: IIF = 0.028 x AEff x C x I.
IIF leakage severity coefficient C | IIF_C | 1.2 | - | WSA 02 Table B1: 0.4 (low) to 1.6 (high). Original sheet 1.2.
1-hour rainfall intensity at 39.35% AEP | I_12 | 21.4 | mm/h | Eqn 3.4.4.2: I = I(1 hour, 39.35% AEP) x (40/NSA)^0.12 x 1.5. Look the intensity up on the Bureau of Meteorology Design Rainfall Data System for the site. 21.4 is the original spreadsheet figure, not a constant printed in STD-SPE-G-011.
FactorSize reference area | I_area_ref | 40 | ha | FactorSize = (40/A)^0.12 (WSA 02 App B4).
FactorSize exponent | I_area_exp | 0.12 | -
FactorContainment | F_cont | 1.5 | - | WSA 02 Table B3: 1.5 for 10-year ARI containment (SW minimum). Original sheet 1.5.
AEff density reference | Dens_ref | 150 | EP/ha | AEff = A x (Density/150)^0.5 for Density < 150 EP/ha, else AEff = A (WSA 02 App B4).
Density basis for AEff (1 = EP/ha per WSA 02; 0 = dwellings/ha as original sheet) | Dens_basis | 1 | - | WSA 02 defines Density as EP per gross hectare. The original sheet used dwellings/ha, and dropped the factor only where dwellings/ha > 150.
EP per dwelling by dwelling density (original sheet lookup)
Low density threshold (< this = low) | Dens_low | 25 | dw/ha
High density threshold (> this = high) | Dens_high | 80 | dw/ha
EP/dwelling - low density | EP_low | 3.5 | EP | Table IW.1: low density, under 25 dwellings per hectare NSA.
EP/dwelling - medium density | EP_med | 2.5 | EP
EP/dwelling - high density | EP_high | 2 | EP

## Peak Flows
Design flow estimation by precinct - WSA 02 Appendix B model (PDWF + GWI + IIF)
Inputs: precinct id, dwellings, area (ha). EP/dwelling is looked up from dwelling density. Coefficients live on 'Parameters'. PWWF here = WSA 02 'design flow' = PDWF + GWI + IIF (the original sheet called IIF 'RDI').
Precinct | Dwellings | Area (ha) | Dwelling density (dw/ha) | EP / dwelling | Total EP | EP density (EP/ha) | ADWF (L/s) | Peaking factor d | PDWF (L/s) | GWI (L/s) | AEff factor | I (mm/h) | IIF / RDI (L/s) | PWWF = design flow (L/s)
1 | 78 | 1.54
2 | 207 | 2.25
3 | 156 | 0.8
4 | 124 | 0.44
5 | 159 | 0.84
6 | 175 | 1.38
7 | 121 | 1.04
8 | 42 | 0.358
9 | 30 | 0.71
10 | 0 | 3.19
Sum of precincts
Combined system (peaking factor on total EP / total area)
Notes: (1) the peaking factor falls with EP (or area), so summing precinct PDWFs over-estimates the PDWF of the combined catchment - use the 'Combined system' row for a trunk serving all precincts (the original summed PWWF = 28.2 L/s). (2) Precinct 10 (0 dwellings) previously gave #DIV/0!. (3) With the original settings (PF_method 1, Dens_basis 0, PortionWet applied once) precinct 2 gives PDWF 2.75 L/s and PWWF 5.48 L/s (original 5.47 - the 0.01 difference is the GWI double-factor).

## Grade Calculator
Minimum and maximum sewer grade by pipe size - Icon Water (ACT) STD-SPE-G-011, supplement to WSA 02-2014 - explicit solution, no Wolfram Alpha
ACT only. Grades are in % (1.000 = 1 % = 1 in 100). Use 'Solve for' to pick the unknown: Grade (from flow and DN), Flow (from a grade and DN), or Diameter (smallest DN whose minimum grade is no steeper than the grade you can build). The table below is always the grade-from-flow direction for every DN.
Precinct (from 'Peak Flows') |  | 2 |  | Legend: | input | calculated |  | Solve for | Grade
Manual EP override (0 = use precinct) |  | 0 | [5 empty] | DN | 225
Manual PDWF override (L/s, 0 = off) |  | 0 | [5 empty] | Grade (%) — input for Flow and Diameter | 1
Manual PWWF override (L/s, 0 = off) |  | 0
EP used | [7 empty] | Answer
PDWF used (L/s) | [7 empty] | What the answer is
PWWF used (L/s) - capacity check only | [7 empty] | Also
Qdmp = f_sss x (PDWF + 2/3 TPF) (L/s) | [7 empty] | Also means
Q for self-cleansing = same Qdmp (L/s) | [7 empty] | Self-cleansing flow at the same grade (L/s Qdmp)
Total pumped flow TPF (L/s, 0 if none) |  | 0
DN150 only: ultimate houses draining to the line |  | Sulphide slime control Sss = K_sss / Rp at f_sss x PDWF (Eq IW.5.5.3.2 / 3.3) | [7 empty] | Self-cleansing Ssc = K_sc / Rp at f_sc x PDWF (Eq IW.5.5.3.1 - verify K_sc) | [5 empty] | Governing minimum grade |  |  |  | Maximum grade (V = V_max at PDWF, IW.5.5.4) | [5 empty] | Capacity check at the governing minimum grade (PWWF)
DN | D (m) | Q75 (L/s) | theta (rad) | y (mm) | y/D | Rp (m) | V (m/s) | Sss (%) | Sss (1 in) | Qsc (L/s) | theta (rad) | y/D | Rp (m) | V (m/s) | Ssc (%) | Absolute min (%) 80/ID or Table IW.4 | Governing Smin (%) | Smin (1 in) | Governing criterion | A = PDWF/V_max (m2) | theta (rad) | y/D | R (m) | Smax (%) | Smax (1 in) | Q full at Smin (L/s) | PWWF / Qfull | y/D at PWWF | V at PWWF (m/s) | PDWF / Qfull | Status
150
225
300
375
450
525
600
675
750
900
Notes
1. Icon Water Eq IW.5.5.3.2 (Sss = 0.0338/Rp) is a tractive-force criterion. Substituting S = K/Rp into Manning removes S: Q = (1/n) sqrt(K/100) A Rp^(1/6). Sheet 'Calc' solves this for the part-full angle theta; Rp and S then follow directly. This replaces the Wolfram Alpha step of the original sheet.
2. Solve for: Grade uses the table. Flow uses Rp = K/grade, then Manning, so a known grade returns the Qdmp at which that grade is exactly Sss (and, beside it, Ssc). Diameter returns the smallest DN that meets the grade you can build. Assuming a depth instead, on Design Table, needs no iteration at all.
3. Both grades use the same flow Qdmp (Eq IW.5.5.3.3). Ssc = 0.0135/Rp and Sss = 0.0338/Rp (Eqs IW.5.5.3.1 and 3.2). Absolute minimum for DN>150 is 80/ID with ID in mm (Eq IW.5.5.3.4). DN150 uses Table IW.4 by number of houses, not those equations.
4. Capacity: the design flow (PWWF) should be carried without surcharge. y/D and PDWF/Qfull are reported so a stricter limit can be applied if Icon requires one.
5. This workbook is for Icon Water (ACT) only. NSW and most other states publish a grade table or a different test, so those numbers are not calculated here.

## Calc
Iteration engine (do not edit). Each block solves the central angle theta of the part-full circle: an asymptotic starting value followed by 14 Newton steps in log-space on f(theta) = A(theta) * R(theta)^m = T. The last column of each block feeds 'Grade Calculator'.
Block 1: slime control (m = 1/6, T1 = Q75 n / sqrt(K_sss/100)) ¦ Block 2: self-cleansing (m = 1/6, K_sc) ¦ Block 3: wetted area for V_max (m = 0, T3 = PDWF/V_max) ¦ Block 4: Manning normal depth at PWWF on the governing grade (m = 2/3, T4 = PWWF n / sqrt(S)). 14 steps give about 1e-6 or better up to y/D = 0.97; beyond that the pipe is reported as too small for the flow.
DN | D (m) | T1 | theta0 | step 1 | step 2 | step 3 | step 4 | step 5 | step 6 | step 7 | step 8 | step 9 | step 10 | step 11 | step 12 | step 13 | step 14 | T2 | theta0 | step 1 | step 2 | step 3 | step 4 | step 5 | step 6 | step 7 | step 8 | step 9 | step 10 | step 11 | step 12 | step 13 | step 14 | A_target (Vmax) | theta0 | step 1 | step 2 | step 3 | step 4 | step 5 | step 6 | step 7 | step 8 | step 9 | step 10 | step 11 | step 12 | step 13 | step 14 | T4 | theta0 | step 1 | step 2 | step 3 | step 4 | step 5 | step 6 | step 7 | step 8 | step 9 | step 10 | step 11 | step 12 | step 13 | step 14
Reverse: theta from Rp = K/S (grade known)
Sss
Ssc

## Design Table
Reverse-direction design table: choose pipe size and depth ratio -> the flow that satisfies each criterion and the corresponding grade (no iteration at all)
For a given DN and y/D: Q75 is the flow for which that depth gives exactly Sss = K_sss/Rp under Manning; PDWF(Sss) = Q75/f_sss. Qsc / Ssc likewise with K_sc. q* = Q n / (sqrt(K_sss/100) D^(13/6)) is dimensionless and identical for every DN, so one curve covers all diameters.
DN | D (m) | y/D | theta (rad) | A (m2) | P (m) | Rp (m) | Q75 for Sss (L/s) | PDWF (Sss basis) (L/s) | Sss (%) | Sss (1 in) | V at Q75 (m/s) | q* (dimensionless) | Qsc for Ssc (L/s) | PDWF (Ssc basis) (L/s) | Ssc (%)
150 |  | 0.05
150 |  | 0.1
150 |  | 0.15
150 |  | 0.2
150 |  | 0.25
150 |  | 0.3
150 |  | 0.35
150 |  | 0.4
150 |  | 0.45
150 |  | 0.5
150 |  | 0.55
150 |  | 0.6
150 |  | 0.65
150 |  | 0.7
150 |  | 0.75
150 |  | 0.8
150 |  | 0.85
150 |  | 0.9
150 |  | 0.95
150 |  | 1
225 |  | 0.05
225 |  | 0.1
225 |  | 0.15
225 |  | 0.2
225 |  | 0.25
225 |  | 0.3
225 |  | 0.35
225 |  | 0.4
225 |  | 0.45
225 |  | 0.5
225 |  | 0.55
225 |  | 0.6
225 |  | 0.65
225 |  | 0.7
225 |  | 0.75
225 |  | 0.8
225 |  | 0.85
225 |  | 0.9
225 |  | 0.95
225 |  | 1
300 |  | 0.05
300 |  | 0.1
300 |  | 0.15
300 |  | 0.2
300 |  | 0.25
300 |  | 0.3
300 |  | 0.35
300 |  | 0.4
300 |  | 0.45
300 |  | 0.5
300 |  | 0.55
300 |  | 0.6
300 |  | 0.65
300 |  | 0.7
300 |  | 0.75
300 |  | 0.8
300 |  | 0.85
300 |  | 0.9
300 |  | 0.95
300 |  | 1
375 |  | 0.05
375 |  | 0.1
375 |  | 0.15
375 |  | 0.2
375 |  | 0.25
375 |  | 0.3
375 |  | 0.35
375 |  | 0.4
375 |  | 0.45
375 |  | 0.5
375 |  | 0.55
375 |  | 0.6
375 |  | 0.65
375 |  | 0.7
375 |  | 0.75
375 |  | 0.8
375 |  | 0.85
375 |  | 0.9
375 |  | 0.95
375 |  | 1
450 |  | 0.05
450 |  | 0.1
450 |  | 0.15
450 |  | 0.2
450 |  | 0.25
450 |  | 0.3
450 |  | 0.35
450 |  | 0.4
450 |  | 0.45
450 |  | 0.5
450 |  | 0.55
450 |  | 0.6
450 |  | 0.65
450 |  | 0.7
450 |  | 0.75
450 |  | 0.8
450 |  | 0.85
450 |  | 0.9
450 |  | 0.95
450 |  | 1
525 |  | 0.05
525 |  | 0.1
525 |  | 0.15
525 |  | 0.2
525 |  | 0.25
525 |  | 0.3
525 |  | 0.35
525 |  | 0.4
525 |  | 0.45
525 |  | 0.5
525 |  | 0.55
525 |  | 0.6
525 |  | 0.65
525 |  | 0.7
525 |  | 0.75
525 |  | 0.8
525 |  | 0.85
525 |  | 0.9
525 |  | 0.95
525 |  | 1
600 |  | 0.05
600 |  | 0.1
600 |  | 0.15
600 |  | 0.2
600 |  | 0.25
600 |  | 0.3
600 |  | 0.35
600 |  | 0.4
600 |  | 0.45
600 |  | 0.5
600 |  | 0.55
600 |  | 0.6
600 |  | 0.65
600 |  | 0.7
600 |  | 0.75
600 |  | 0.8
600 |  | 0.85
600 |  | 0.9
600 |  | 0.95
600 |  | 1
675 |  | 0.05
675 |  | 0.1
675 |  | 0.15
675 |  | 0.2
675 |  | 0.25
675 |  | 0.3
675 |  | 0.35
675 |  | 0.4
675 |  | 0.45
675 |  | 0.5
675 |  | 0.55
675 |  | 0.6
675 |  | 0.65
675 |  | 0.7
675 |  | 0.75
675 |  | 0.8
675 |  | 0.85
675 |  | 0.9
675 |  | 0.95
675 |  | 1
750 |  | 0.05
750 |  | 0.1
750 |  | 0.15
750 |  | 0.2
750 |  | 0.25
750 |  | 0.3
750 |  | 0.35
750 |  | 0.4
750 |  | 0.45
750 |  | 0.5
750 |  | 0.55
750 |  | 0.6
750 |  | 0.65
750 |  | 0.7
750 |  | 0.75
750 |  | 0.8
750 |  | 0.85
750 |  | 0.9
750 |  | 0.95
750 |  | 1
900 |  | 0.05
900 |  | 0.1
900 |  | 0.15
900 |  | 0.2
900 |  | 0.25
900 |  | 0.3
900 |  | 0.35
900 |  | 0.4
900 |  | 0.45
900 |  | 0.5
900 |  | 0.55
900 |  | 0.6
900 |  | 0.65
900 |  | 0.7
900 |  | 0.75
900 |  | 0.8
900 |  | 0.85
900 |  | 0.9
900 |  | 0.95
900 |  | 1

## Validation
Validation against the original spreadsheet's Wolfram Alpha solutions and published values
Rows 5-9 re-solve the exact cases the original sheet solved in Wolfram Alpha, using the same iteration as 'Calc'. Differences are rounding of the Wolfram values the original typed in.
Case | D (m) | Target T | n | K (%.m) | theta0 | step 1 | step 2 | step 3 | step 4 | step 5 | step 6 | step 7 | step 8 | step 9 | step 10 | step 11 | step 12 | step 13 | step 14 | theta | Result | Expected (original) | Difference
DN300 slime control: y (mm) at Q75 = 4.1015 L/s (0.75 x 5.4686) | 0.3 |  | 0.012 | 0.0338 | [17 empty] | 37
DN300 slime control: Sss (%) for the same case | [21 empty] | 1.4552
DN150 max velocity: y (mm) for A = 0.0018857 m2 (5.4686 L/s at 2.9 m/s) | 0.15 | 0.0018857 | [19 empty] | 24.5518
DN300 max velocity: y (mm) for A = 0.0018857 m2 (5.4686 L/s at 2.9 m/s) | 0.3 | 0.0018857 | [19 empty] | 19.069
DN150 max grade (%) for the same case (original: 32.47 % = 2.9 m/s in DN150 at 5.47 L/s) | [21 empty] | 32.4725
Published Icon Water values (Molonglo 2 sewer report) - implied design flows computed with the same equations (n = 0.012, K_sss = 0.0338):
DN225 SSC grade 0.94 % -> Rp = 0.036 m, y/D = 0.28, Q75 = 7.9 L/s, PDWF ~ 10.5 L/s
DN300 SSC grade 0.54-0.64 % -> y/D = 0.31-0.39, PDWF ~ 23-32 L/s
STD-SPE-G-011 Version 5 fixes the coefficients at Ssc = 0.0135/Rp and Sss = 0.0338/Rp, both at Qdmp. The 0.0163 figure was an earlier guess and is not in the supplement.

## Sources
Sources and further reading (see also RESEARCH_NOTES.md in the repo)
Publisher | Document / relevance | Link
Icon Water | STD-SPE-G-011 Supplement to WSA 02-2014-3.3 Gravity Sewerage Code of Australia (Eq IW.5.5.3.1-3, IW.5.5.4, Table IW.3) - download from the standards page | https://www.iconwater.com.au/Developers-and-Renovators/Water-and-Sewerage-Service-Standards-and-Guidelines/New-Icon-Water-water-supply-and-sewerage-standards
WSAA / Sydney Water | WSA 02-2002-2.2 Sewerage Code of Australia, Sydney Water Edition v3 (2009), Part 1 Planning and Design - cl 3 flow estimation, cl 4.5 pipe sizing and grading, App A EP, App B flow model. In RAG corpus: rag_demo_complete\pdfs\sydney_water\WSA02_2002_Part1_22_SW3.pdf | (local)
WSAA | WSA 02-2014 Gravity Sewerage Code of Australia v3.1 / v3.3 (purchase) | https://www.wsaa.asn.au/
Sydney Water | Design guideline - minimising odour-causing turbulence D0002356 (0.7 m/s; 1.6 Pa grit; 3.35 Pa slime; min grade tables) | https://www.sydneywater.com.au/content/dam/sydneywater/documents/provider-information/standards-specifications/design-guideline-minimising-odour-causing-turbulence.pdf
Sydney Water | Pipe sizing and grading tables (Tables SW 4.1-4.x, EP / grade / capacity) | https://www.sydneywater.com.au/content/dam/sydneywater/documents/provider-information/instructions/pipe-sizing-and-grading-tables.pdf
Standards Australia | AS 2200-2006 Design charts for water supply and sewerage (Colebrook-White / Manning part-full charts) | https://www.standards.org.au/
Standards Australia | AS/NZS 3500.2 Sanitary plumbing and drainage - minimum drain grades (in RAG corpus: AS3500.2-2021.pdf) | (local)
Central Coast Council | WSAA Sewerage Code supplement V1.0 - refers to Hunter Water WSA 02-2014-3.1 App HW R empirical size/grade relationships (in RAG corpus) | (local)
Mara & Broome (2008) | Sewerage: a return to basics to benefit the poor - i_min = K Q^-6/13 from tractive tension + Manning (NBR 9649 form 0.0055 Q^-0.47) | https://eprints.whiterose.ac.uk/
Akgiray (2004, 2005) | Explicit solutions of the Manning equation for partially filled circular pipes (Can. J. Civ. Eng. 32:490-499; Environ. Eng. Sci. 21(3)) | https://doi.org/10.1139/l05-001
Saatci (1990) | Velocity and depth of flow calculations in partially filled pipes, J. Environ. Eng. 116(6) | https://doi.org/10.1061/(ASCE)0733-9372(1990)116:6(1202)
Giroud, Palmer & Dove (2000) | Calculation of flow velocity in pipes as a function of flow rate, Geosynthetics International 7(4-6) | https://doi.org/10.1680/gein.7.0177
Bengtson (PDH) | Partially full pipe flow calculations (SI units) - cited in the original notes | https://pdhlibrary.com/
Engineering Toolbox | Manning's formula and gravity flow - cited in the original notes | https://www.engineeringtoolbox.com/mannings-formula-gravity-flow-d_805.html
Hunter Water | WSA 02-2014-3.1 Hunter Water edition, Appendix HW N (flows) and HW R (empirical pipe sizing / grading) - purchase via WSAA | https://www.hunterwater.com.au/building-and-developing/drawings-plans-and-specifications/water-and-sewer-design-manuals
MRWA / Coliban / TasWater / SGW | WSA 02-2014-3.1 MRWA edition supplements - Table 5.6 min grades, 0.35 m/s at PDWF+GWI, Colebrook-White part-full | https://coliban.com.au/
QLD (FNQROC D7, CMDG D12, Toowoomba) | PDWF = 4.7 EP^-0.105 ADWF; tractive force 0.15 kg/m2 | https://www.fnqroc.qld.gov.au/